## Safety Checklist
S.No. | Category | Safety Parameter & NBC Ref. | NBC Universal Compliance Criteria | Pass | Fail | Remarks / Action Required
1.1 | 1. Egress & Means of Escape | Exit Count & Width | Minimum 2 independent exits per floor. Clear width matching occupancy load factors (e.g., min 1.5m–2.0m for public/assembly areas).
1.2 | 1. Egress & Means of Escape | Travel Distance | Maximum travel distance to a safe exit within 22.5m (hazardous), 30m (normal), or 45m (sprinklered residential/business).
1.3 | 1. Egress & Means of Escape | Staircase Pressurization | Mechanical pressurization fully operational for internal stairwells and lift lobbies in high-rises exceeding 24m in height.
1.4 | 1. Egress & Means of Escape | Refuge Area Access | Dedicated structural refuge area clear of obstructions, provided at the 24m level and every subsequent 15m in high-rise buildings.
1.5 | 1. Egress & Means of Escape | Exit Door Mechanics | All exit doors swing outwards in the direction of escape. Fitted with panic bars where required; no padlocks/chains allowed during occupancy.
2.1 | 2. Fire Detection & Suppression | Fire Alarm System | Automatic smoke/heat detectors installed per IS 2189. Main control panel operational with functional zones & battery backup.
2.2 | 2. Fire Detection & Suppression | Manual Call Points (MCP) | MCP units installed at a standardized height of 1.2m near all exit staircases and lift lobbies, completely unobstructed.
2.3 | 2. Fire Detection & Suppression | Sprinkler Networks | Automatic sprinkler systems fully pressurized per IS 15105 in basements, high-rises, and hazardous occupancies.
2.4 | 2. Fire Detection & Suppression | Wet Riser & Hose Reels | Wet riser pipework charged with water under pressure. First-aid hose reels operational at every floor landing (IS 3844).
2.5 | 2. Fire Detection & Suppression | Dedicated Water Storage | Static underground and overhead fire water tanks maintained at full capacity exclusively for firefighting systems.
3.1 | 3. Portable Fire Extinguishers | Type & Hazard Matching | Extinguishers correctly matched to fire risks (Class A/B/C/D & Electrical) and strategically placed at designated high-risk zones.
3.2 | 3. Portable Fire Extinguishers | Placement & Spacing | Extinguishers distributed within a maximum travel distance of 15m. Mounted at a visible height between 1.0m to 1.5m.
3.3 | 3. Portable Fire Extinguishers | Maintenance & Tagging | Annual servicing, hydraulic testing, and weight checks completed as per IS 2190 guidelines with valid inspection tags.
4.1 | 4. Passive Fire Protection | Fire-Rated Doors (FCHD) | Fire doors at stairwells, lift lobbies, and high-hazard rooms certified for minimum 1 to 2-hour fire resistance rating.
4.2 | 4. Passive Fire Protection | Compartmentation Seals | All vertical shafts, cable trays, and plumbing pipe penetrations sealed completely using certified intumescent firestops.
4.3 | 4. Passive Fire Protection | Interior Finishes | Wall linings, acoustic paneling, and false ceiling materials comply with low flame-spread characteristics defined by the NBC.
5.1 | 5. Electrical & High-Risk Zones | Electrical Shafts | Electrical ducts/shafts sealed at every floor level with non-combustible materials. Free of any storage or debris.
5.2 | 5. Electrical & High-Risk Zones | Emergency Power Supply | Auto-changeover Diesel Generator (DG) set functional. Powers emergency lifts, stairwell lights, and fire pumps within 15 seconds of grid failure.
5.3 | 5. Electrical & High-Risk Zones | EV Charging Isolation | EV charging bays isolated from primary building structures by a minimum 3m setback or protected by localized automatic sprinklers.
5.4 | 5. Electrical & High-Risk Zones | Thermal Imaging Audits | Periodic infrared thermography audits completed for main LT/HT panels and distribution boards to eliminate latent hot spots.
6.1 | 6. Specialized Hazards & Systems | Kitchen Suppression System | Commercial kitchen hoods fitted with automatic wet chemical suppression systems. Interlocked to automatically shut off gas/fuel supply upon activation.
6.2 | 6. Specialized Hazards & Systems | Server/Data Room Flooding | Server rooms and critical IT infrastructure equipped with automated gaseous flooding systems (e.g., FM200/Novec 1230). Room integrity tested annually.
6.3 | 6. Specialized Hazards & Systems | Basement Smoke Extraction | Mechanical smoke extraction system fully functional in basements. Delivers minimum 30 air changes per hour (ACH) under emergency fire mode operations.
7.1 | 7. Emergency Signage & Protocols | Photoluminescent Signs | Exit signage clearly visible along paths, changes of direction, and doors. Self-luminous or connected to emergency circuits.
7.2 | 7. Emergency Signage & Protocols | Emergency Lighting | Automatic emergency lights operational along all corridors, basements, and staircases, providing minimum 1-hour runtime.
7.3 | 7. Emergency Signage & Protocols | Evacuation Drills | Mandatory fire evacuation drills conducted at least biannually for all occupants, logged systematically with structural marshals.
7.4 | 7. Emergency Signage & Protocols | Third-Party Audits | Fire safety audit executed and certified by an accredited external agency within the legally mandated statutory cycles.